## Without damper Initial design
Section | Length (m) | Velocity (m/s) | Flow Rate (m3/s) | hl (Pa/m) | Hv (Pa) | HI (Pa) | De (mm) | Possible rectangular dimensions
A | 15.2 | 4.3 | 2.28 | 0.23 | 11.1284 | 3.496 | 795 | • 775 (30.5) → (30in X 26in) • 805 (31.7) → (30in X 28in) • 777 (30.6) → (28in X 28in) • 833 (32.8) → (30in X 30in)
B | 10.7 | 6.1 | 2.28 | 0.58 | 22.3951 | 6.206 | 688 | • 676 (26.6) → (30in X 20in) • 688 (27.1) → (28in X 22in) • 693 (27.3) → (26in X 24in)
C | 6.1 | 4.9 | 1.14 | 0.55 | 14.4506 | 3.355 | 525 | • 526 (20.7) → (30in X 12in) • 526 (20.7) → (20in X 18in) • 523 (20.6) → (26in X 14in) • 518 (20.4) → (22in X 16in)
D | 5.5 | 4 | 0.57 | 0.45 | 9.6297 | 2.475 | 420 | • 409 (16.1) → (30in X 8in) • 419 (16.5) → (24in X 10in) • 426 (16.8) → (20in X 12in) • 417 (16.4) → (16in X 14in)
E | 9.1 | 4.9 | 0.57 | 0.78 | 14.4506 | 7.098 | 375 | • 384 (15.1) → (26in X 8in) • 371 (14.6) → (24in X 8in) • 368 (14.5) → (18in X 10in) • 386 (15.2) → (20in X 10in) • 361 (14.2) → (14in X 12in) • 384 (15.1) → (16in X 12in) • 389 (15.3) → (14in X 14in)
F | 5.5 | 4 | 0.57 | 0.45 | 9.6297 | 2.475 | 420 | • 409 (16.1) → (30in X 8in) • 419 (16.5) → (24in X 10in) • 426 (16.8) → (20in X 12in) • 417 (16.4) → (16in X 14in)
G | 12.2 | 6.1 | 1.14 | 0.93 | 22.3951 | 11.346 | 465 | • 465 (18.3) → (30in X 10in) • 465 (18.3) → (24in X 12in) • 462 (18.2) → (20in X 14in) • 470 (18.5) → (18in X 16in)
H | 6.1 | 4.9 | 1.14 | 0.55 | 14.4506 | 3.355 | 525 | • 526 (20.7) → (30in X 12in) • 526 (20.7) → (20in X 18in) • 523 (20.6) → (26in X 14in) • 518 (20.4) → (22in X 16in)
I | 5.5 | 4 | 0.57 | 0.45 | 9.6297 | 2.475 | 420 | • 409 (16.1) → (30in X 8in) • 419 (16.5) → (24in X 10in) • 426 (16.8) → (20in X 12in) • 417 (16.4) → (16in X 14in)
J | 9.1 | 4.9 | 0.57 | 0.78 | 14.4506 | 7.098 | 375 | • 384 (15.1) → (26in X 8in) • 371 (14.6) → (24in X 8in) • 368 (14.5) → (18in X 10in) • 386 (15.2) → (20in X 10in) • 361 (14.2) → (14in X 12in) • 384 (15.1) → (16in X 12in) • 389 (15.3) → (14in X 14in)
K | 5.5 | 4 | 0.57 | 0.45 | 9.6297 | 2.475 | 420 | • 409 (16.1) → (30in X 8in) • 419 (16.5) → (24in X 10in) • 426 (16.8) → (20in X 12in) • 417 (16.4) → (16in X 14in)
Elbow | Velocity | C | Hv | HL |  | Grille | HL
Elbow in C | 4.9 | 0.18 | 14.4506 | 2.6011 |  | Duct D | 15
Elbow in F | 4 | 0.18 | 9.6297 | 1.7334 |  | Duct F | 15
Elbow in H | 4.9 | 0.18 | 14.4506 | 2.6011 |  | Duct I | 15
Elbow in K | 4 | 0.18 | 9.6297 | 1.7334 |  | Duct K | 15
Elbow to grille (D) | 4 | 0.18 | 9.6297 | 1.7334
Elbow to grille (F) | 4 | 0.18 | 9.6297 | 1.7334 |  | Intake | Size (m) | K (Well Rounded) | Flow Rate | Velocity (m/s) | HL (Pressure drop) (Kpa) | hl
Elbow to grille (I) | 4 | 0.18 | 9.6297 | 1.7334 |  | Gradual Contraction | 1 x 1 | 0.04 | 2.28 | 4.3 | 17 | 0.037696
Elbow to grille (K) | 4 | 0.18 | 9.6297 | 1.7334
T Section | Velocity | C | Hv | HL
T to duct C from B (Branch) | 6.1 | 1 | 22.3951 | 22.3951
T to duct D from C (branch) | 4.9 | 1 | 14.4506 | 14.4506
T to duct G from B (flow through Mains) | 6.1 | 0.1 | 22.3951 | 2.2395
T to duct I from H (Branch) | 4.9 | 1 | 14.4506 | 14.4506
Path 1 |  |  | Path 2
Section | Loss (Pa) |  | Section | Loss (Pa)
B | 6.206 |  | B | 6.206
Elbow in C | 2.6011 |  | Elbow in C | 2.6011
T to duct C from B (Branch) | 22.3951 |  | C | 3.355
C | 3.355 |  | T to duct C from B (Branch) | 22.3951
T to duct D from C (branch) | 14.4506 |  | E | 7.098
Elbow to grille (D) | 1.7334 |  | Elbow to grille (F) | 1.7334
D | 2.475 |  | Elbow in F | 1.7334
Grill in D | 15 |  | Grill in F | 15
Total Loss | 68.2162 |  | F | 2.475
|  |  | Total Loss | 62.597
Path 3 |  |  | Path 4
Section | Loss (Pa) |  | Section | Loss
B | 6.206 |  | B | 6.206
T to duct G from B (flow through Mains) | 2.2395 |  | T to duct G from B (flow through Mains) | 2.2395
G | 11.346 |  | G | 11.346
Elbow in H | 2.6011 |  | Elbow in H | 2.6011
H | 3.355 |  | H | 3.355
T to duct I from H (Branch) | 14.4506 |  | J | 7.098
Elbow to grille (I) | 1.7334 |  | Elbow to grille (K) | 1.7334
I | 2.475 |  | Elbow in K | 1.7334
Grill in I | 15 |  | K | 2.475
Total Loss | 59.4066 |  | Grill in K | 15
|  |  | Total Loss | 53.7873

## With Damper
Section | Length (m) | Velocity (m/s) | Flow Rate (m3/s) | hl (Pa/m) | Hv (Pa) | HI (Pa) | De (mm)
A | 15.2 | 4.3 | 2.28 | 0.23 | 11.1284 | 3.496 | 795
B | 10.7 | 6.1 | 2.28 | 0.58 | 22.3951 | 6.206 | 688
C | 6.1 | 4.9 | 1.14 | 0.55 | 14.4506 | 3.355 | 525
D | 5.5 | 4 | 0.57 | 0.45 | 9.6297 | 2.475 | 420
E | 9.1 | 4.9 | 0.57 | 0.78 | 14.4506 | 7.098 | 375
F | 5.5 | 4 | 0.57 | 0.45 | 9.6297 | 2.475 | 420
G | 12.2 | 6.1 | 1.14 | 0.93 | 22.3951 | 11.346 | 465
H | 6.1 | 4.9 | 1.14 | 0.55 | 14.4506 | 3.355 | 525
I | 5.5 | 4 | 0.57 | 0.45 | 9.6297 | 2.475 | 420
J | 9.1 | 4.9 | 0.57 | 0.78 | 14.4506 | 7.098 | 375
K | 5.5 | 4 | 0.57 | 0.45 | 9.6297 | 2.475 | 420
Elbow | Velocity | C | Hv | HL |  | Grill | HL
Elbow in C | 4.9 | 0.18 | 14.4506 | 2.6011 |  | Duct D | 15
Elbow in F | 4 | 0.18 | 9.6297 | 1.7334 |  | Duct F | 15
Elbow in H | 4.9 | 0.18 | 14.4506 | 2.6011 |  | Duct I | 15
Elbow in K | 4 | 0.18 | 9.6297 | 1.7334 |  | Duct K | 15
Elbow to grille (D) | 4 | 0.18 | 9.6297 | 1.7334
Elbow to grille (F) | 4 | 0.18 | 9.6297 | 1.7334 |  | Intake | Size (m) | K (Well Rounded) | Flow Rate | Velocity (m/s) | HL (Pressure drop) (Kpa) | hl
Elbow to grille (I) | 4 | 0.18 | 9.6297 | 1.7334 |  | Gradual Contraction | 1 x 1 | 0.04 | 2.28 | 4.3 | 17 | 0.037696
Elbow to grille (K) | 4 | 0.18 | 9.6297 | 1.7334
T Section | Velocity | C | Hv | HL |  | Damper | Velocity | C | Hv | HL
T to duct C from B (Branch) | 6.1 | 1 | 22.3951 | 22.3951 |  | Damper in duct A | 4.3 | 0.2 | 11.1284 | 2.2257
T to duct D from C (branch) | 4.9 | 1 | 14.4506 | 14.4506 |  | Damper in duct D | 4 | 0.2 | 9.6297 | 1.9259
T to duct G from B (flow through Mains) | 6.1 | 0.1 | 22.3951 | 2.2395 |  | Damper in duct F | 4 | 0.2 | 9.6297 | 1.9259
T to duct I from H (Branch) | 4.9 | 1 | 14.4506 | 14.4506 |  | Damper in duct I | 4 | 0.2 | 9.6297 | 1.9259
[6 empty] | Damper in duct K | 4 | 0.2 | 9.6297 | 1.9259
Path 1 |  |  | Path 2
Section | Loss (Pa) |  | Section | Loss (Pa)
B | 6.206 |  | B | 6.206
Elbow in C | 2.6011 |  | Elbow in C | 2.6011
T to duct C from B (Branch) | 22.3951 |  | C | 3.355
C | 3.355 |  | T to duct C from B (Branch) | 22.3951
T to duct D from C (branch) | 14.4506 |  | E | 7.098
D | 2.475 |  | Elbow in F | 1.7334
Damper in duct D | 1.9259 |  | Damper in duct F | 1.9259
Elbow to grille (D) | 1.7334 |  | Elbow to grille (F) | 1.7334
Grill in D | 15 |  | Grill in F | 15
Total Loss | 70.1422 |  | F | 2.475
|  |  | Total Loss | 64.5229
Path 3 |  |  | Path 4
Section | Loss (Pa) |  | Section | Loss
B | 6.206 |  | B | 6.206
T to duct G from B (flow through Mains) | 2.2395 |  | T to duct G from B (flow through Mains) | 2.2395
G | 11.346 |  | G | 11.346
Elbow in H | 2.6011 |  | Elbow in H | 2.6011
H | 3.355 |  | H | 3.355
T to duct I from H (Branch) | 14.4506 |  | J | 7.098
Damper in duct I | 1.9259 |  | Damper in duct K | 1.9259
Elbow to grille (I) | 1.7334 |  | Elbow to grille (K) | 1.7334
I | 2.475 |  | Elbow in K | 1.7334
Grill in I | 15 |  | K | 2.475
Total Loss | 61.3325 |  | Grill in K | 15
|  |  | Total Loss | 55.7133

## Velocity
Section | Length (m) | Velocity (m/s) | Flow Rate (m3/s) | hl (Pa/m) | Hv (Pa) | HI (Pa) | De (mm) | Preffered duct size
A | 15.2 | 4.3 | 2.28 | 0.23 | 11.1284 | 3.496 | 800 | • 805 (31.7) → (30in X 28in) • 833 (32.8) → (30in X 30in) • 777 (30.6) → (28in X 28in)
B | 10.7 | 8 | 2.28 | 1.25 | 38.5189 | 13.375 | 600 | • 600 (23.7) → (30in X 16in) • 597 (23.5) → (26in X 18in) • 620 (24.4) → (28in X 18in) • 607 (23.4) → (24in X 20in) • 610 (24) → (22in X 22in)
C | 6.1 | 4 | 1.14 | 0.29 | 9.6297 | 1.769 | 580 | • 582 (22.9) → (28in X 16in) • 577 (22.7) → (24in X 18in) • 562 (22.9) → (22in X 20in) • 561 (22.1) → (26in X 16in)
D | 5.5 | 3.3 | 0.57 | 0.28 | 6.5542 | 1.54 | 475 | • 465 (18.3) → (30in X 10in) • 465 (18.3) → (24in X 12in) • 483 (19) → (26in X 12in) • 462 (18.2) → (20in X 14in) • 485 (19.1) → (22in X 14in) • 470 (18.5) → (18in X 16in)
E | 9.1 | 3.9 | 0.57 | 0.41 | 9.1543 | 3.731 | 430 | • 434 (17.1) → (26in X 10in) • 426 (16.8) → (20in X 12in) • 417 (16.4) → (16in X 14in) • 439 (17.3) → (18in X 14in)
F | 5.5 | 3.9 | 0.57 | 0.41 | 9.1543 | 2.255 | 430 | • 434 (17.1) → (26in X 10in) • 426 (16.8) → (20in X 12in) • 417 (16.4) → (16in X 14in) • 439 (17.3) → (18in X 14in)
G | 12.2 | 6.1 | 1.14 | 0.89 | 22.3951 | 10.858 | 580 | • 582 (22.9) → (28in X 16in) • 577 (22.7) → (24in X 18in) • 562 (22.9) → (22in X 20in) • 561 (22.1) → (26in X 16in)
H | 6.1 | 6.1 | 1.14 | 0.89 | 22.3951 | 5.429 | 580 | • 582 (22.9) → (28in X 16in) • 577 (22.7) → (24in X 18in) • 562 (22.9) → (22in X 20in) • 561 (22.1) → (26in X 16in)
I | 5.5 | 5 | 0.57 | 0.75 | 15.0465 | 4.125 | 375 | • 371 (14.6) → (24in X 8in) • 384 (15.1) → (26in X 8in) • 368 (14.5) → (18in X 10in) • 386 (15.2) → (20in X 10in) • 361 (14.2) → (14in X 12in) • 384 (15.1) → (16in X 12in) • 389 (15.3) → (14in X 14in)
J | 9.1 | 5.4 | 0.57 | 1.1 | 17.5502 | 10.01 | 360 | • 358 (14.1) → (22in X 8in) • 371 (14.6) → (24in X 8in) • 368 (14.5) → (18in X 10in) • 361 (14.2) → (20in X 14in) • 361 (14.2) → (14in X 12in)
K | 5.5 | 5.4 | 0.57 | 1.1 | 17.5502 | 6.05 | 360 | • 358 (14.1) → (22in X 8in) • 371 (14.6) → (24in X 8in) • 368 (14.5) → (18in X 10in) • 361 (14.2) → (20in X 14in) • 361 (14.2) → (14in X 12in)
Elbow | Velocity | C | Hv | HL |  | Grill | HL
Elbow in C | 4 | 0.18 | 9.6297 | 1.7334 |  | Duct D | 15
Elbow in F | 3.9 | 0.18 | 9.1543 | 1.6478 |  | Duct F | 15
Elbow in H | 6.1 | 0.18 | 22.3951 | 4.0311 |  | Duct I | 15
Elbow in K | 5.4 | 0.18 | 17.5502 | 3.159 |  | Duct K | 15
Elbow to grille (D) | 3.3 | 0.18 | 6.5542 | 1.1798
Elbow to grille (F) | 3.9 | 0.18 | 9.1543 | 1.6478 |  | Intake | Size (m) | K (Well Rounded) | Flow Rate | Velocity (m/s) | HL (Pressure drop) (Kpa) | hl
Elbow to grille (I) | 5 | 0.18 | 15.0465 | 2.7084 |  | Gradual Contraction | 1 x 1 | 0.04 | 2.28 | 4.3 | 17 | 0.037696
Elbow to grille (K) | 5.4 | 0.18 | 17.5502 | 3.159
T Section | Velocity | C | Hv | HL |  | Damper | Velocity | C | Hv | HL
T to duct C from B (Branch) | 8 | 1 | 38.5189 | 38.5189 |  | Damper in duct A | 4.3 | 0.2 | 11.1284 | 2.2257
T to duct D from C (branch) | 4 | 1 | 9.6297 | 9.6297 |  | Damper in duct D | 3.3 | 0.2 | 6.5542 | 1.3108
T to duct G from B (flow through Mains) | 8 | 0.1 | 38.5189 | 3.8519 |  | Damper in duct F | 3.9 | 0.52 | 9.1543 | 4.7602
T to duct I from H (Branch) | 6.1 | 1 | 22.3951 | 22.3951 |  | Damper in duct I | 5 | 0.2 | 15.0465 | 3.0093
[6 empty] | Damper in duct K | 5.4 | 0.52 | 17.5502 | 9.1261
Path 1 |  |  | Path 2
Section | Loss (Pa) |  | Section | Loss (Pa)
B | 13.375 |  | B | 13.375
Elbow in C | 1.7334 |  | Elbow in C | 1.7334
T to duct C from B (Branch) | 38.5189 |  | C | 1.769
C | 1.769 |  | T to duct C from B (Branch) | 38.5189
T to duct D from C (branch) | 9.6297 |  | E | 3.731
D | 1.54 |  | Elbow in F | 1.6478
Elbow to grille (D) | 1.1798 |  | Elbow to grille (F) | 1.6478
Damper in duct D | 1.3108 |  | Damper in duct F | 4.7602
Grill in D | 15 |  | Grill in F | 15
Total Loss | 84.0566 |  | F | 2.255
|  |  | Total Loss | 84.438
Path 3 |  |  | Path 4
Section | Loss (Pa) |  | Section | Loss
B | 13.375 |  | B | 13.375
T to duct G from B (flow through Mains) | 3.8519 |  | T to duct G from B (flow through Mains) | 3.8519
G | 10.858 |  | G | 10.858
Elbow in H | 4.0311 |  | Elbow in H | 4.0311
H | 5.429 |  | H | 5.429
T to duct I from H (Branch) | 22.3951 |  | J | 10.01
Damper in duct I | 3.0093 |  | Damper in duct K | 9.1261
Elbow to grille (I) | 2.7084 |  | Elbow to grille (K) | 3.159
I | 4.125 |  | Elbow in K | 3.159
Grill in I | 15 |  | K | 6.05
Total Loss | 84.7828 |  | Grill in K | 15
|  |  | Total Loss | 84.0492

## Constant Friction Factor Design
Section | Length (m) | Velocity (m/s) | Flow Rate (m3/s) | hl (Pa/m) | Hv (Pa) | HI (Pa) | De (mm) | Available Duct Size
A | 15.2 | 8 | 2.28 | 1.25 | 38.5189 | 19 | 600 | • 600 (23.7) → (30in X 16in) • 597 (23.5) → (26in X 18in) • 620 (24.4) → (28in X 18in) • 607 (23.4) → (24in X 20in) • 610 (24) → (22in X 22in)
B | 10.7 | 8 | 2.28 | 1.25 | 38.5189 | 13.375 | 600 | • 600 (23.7) → (30in X 16in) • 597 (23.5) → (26in X 18in) • 620 (24.4) → (28in X 18in) • 607 (23.4) → (24in X 20in) • 610 (24) → (22in X 22in)
C | 6.1 | 7 | 1.14 | 1.25 | 29.4911 | 7.625 | 450 | • 450 (17.7) → (28in X 10in) • 447 (17.6) → (22in X 12in) • 445 (17.5) → (16in X 16in)
D | 5.5 | 5.8 | 0.57 | 1.25 | 20.2465 | 6.875 | 350 | • 345 (13.6) → (30in X 6in) • 342 (13.5) → (20in X 8in) • 358 (14.1) → (22in X 8in) • 348 (13.7) → (16in X 10in)
E | 9.1 | 5.6 | 0.57 | 1.1 | 18.8743 | 10.01 | 350 | • 345 (13.6) → (30in X 6in) • 342 (13.5) → (20in X 8in) • 358 (14.1) → (22in X 8in) • 348 (13.7) → (16in X 10in)
F | 5.5 | 5.6 | 0.57 | 1.1 | 18.8743 | 6.05 | 350 | • 345 (13.6) → (30in X 6in) • 342 (13.5) → (20in X 8in) • 358 (14.1) → (22in X 8in) • 348 (13.7) → (16in X 10in)
G | 12.2 | 7 | 1.14 | 1.25 | 29.4911 | 15.25 | 450 | • 450 (17.7) → (28in X 10in) • 447 (17.6) → (22in X 12in) • 445 (17.5) → (16in X 16in)
H | 6.1 | 7 | 1.14 | 1.25 | 29.4911 | 7.625 | 450 | • 450 (17.7) → (28in X 10in) • 447 (17.6) → (22in X 12in) • 445 (17.5) → (16in X 16in)
I | 5.5 | 5.8 | 0.57 | 1.25 | 20.2465 | 6.875 | 350 | • 345 (13.6) → (30in X 6in) • 342 (13.5) → (20in X 8in) • 358 (14.1) → (22in X 8in) • 348 (13.7) → (16in X 10in)
J | 9.1 | 6 | 0.57 | 1.3 | 21.6669 | 11.83 | 350 | • 345 (13.6) → (30in X 6in) • 342 (13.5) → (20in X 8in) • 358 (14.1) → (22in X 8in) • 348 (13.7) → (16in X 10in)
K | 5.5 | 6 | 0.57 | 1.3 | 21.6669 | 7.15 | 350 | • 345 (13.6) → (30in X 6in) • 342 (13.5) → (20in X 8in) • 358 (14.1) → (22in X 8in) • 348 (13.7) → (16in X 10in)
Elbow | Velocity | C | Hv | HL |  | Grill | HL
Elbow in C | 7 | 0.18 | 29.4911 | 5.3084 |  | Duct D | 15
Elbow in F | 5.6 | 0.18 | 18.8743 | 3.3974 |  | Duct F | 15
Elbow in H | 7 | 0.18 | 29.4911 | 5.3084 |  | Duct I | 15
Elbow in K | 6 | 0.18 | 21.6669 | 3.9 |  | Duct K | 15
Elbow to grille (D) | 5.8 | 0.18 | 20.2465 | 3.6444
Elbow to grille (F) | 5.6 | 0.18 | 18.8743 | 3.3974 |  | Intake | Size (m) | K (Well Rounded) | Flow Rate | Velocity (m/s) | HL (Pressure drop) (Kpa) | hl
Elbow to grille (I) | 5.8 | 0.18 | 20.2465 | 3.6444 |  | Gradual Contraction | 1 x 1 | 0.04 | 2.28 | 4.3 | 17 | 0.037696
Elbow to grille (K) | 6 | 0.18 | 21.6669 | 3.9
T Section | Velocity | C | Hv | HL |  | Damper | Velocity | C | Hv | HL
T to duct C from B (Branch) | 8 | 1 | 38.5189 | 38.5189 |  | Damper in duct A | 8 | 0.2 | 38.5189 | 7.7038
T to duct D from C (branch) | 7 | 1 | 29.4911 | 29.4911 |  | Damper in duct D | 5.8 | 0.52 | 20.2465 | 10.5282
T to duct G from B (flow through Mains) | 8 | 0.1 | 38.5189 | 3.8519 |  | Damper in duct F | 5.6 | 1.5 | 18.8743 | 28.3114
T to duct I from H (Branch) | 7 | 1 | 29.4911 | 29.4911 |  | Damper in duct I | 5.8 | 1.5 | 20.2465 | 30.3698
[6 empty] | Damper in duct K | 6 | 1.5 | 21.6669 | 32.5003
[6 empty] | Damper in duct J | 6 | 0.52 | 21.6669 | 11.2668
Path 1 |  |  | Path 2
Section | Loss (Pa) |  | Section | Loss (Pa)
B | 13.375 |  | B | 13.375
Elbow in C | 5.3084 |  | Elbow in C | 5.3084
T to duct C from B (Branch) | 38.5189 |  | C | 7.625
C | 7.625 |  | T to duct C from B (Branch) | 38.5189
T to duct D from C (branch) | 29.4911 |  | E | 10.01
D | 6.875 |  | Elbow in F | 3.3974
Damper in Duct D | 10.5282 |  | Damper in duct F | 28.3114
Elbow to grille (D) | 3.6444 |  | Elbow to grille (F) | 3.3974
Grill in D | 15 |  | Grill in F | 15
Total Loss | 130.3659 |  | F | 6.05
|  |  | Total Loss | 130.9935
Path 3 |  |  | Path 4
Section | Loss (Pa) |  | Section | Loss
B | 13.375 |  | B | 13.375
T to duct G from B (flow through Mains) | 3.8519 |  | T to duct G from B (flow through Mains) | 3.8519
G | 15.25 |  | G | 15.25
Elbow in H | 5.3084 |  | Elbow in H | 5.3084
H | 7.625 |  | H | 7.625
T to duct I from H (Branch) | 29.4911 |  | J | 11.83
Damper in duct I | 30.3698 |  | Damper in duct K | 32.5003
I | 6.875 |  | Elbow in K | 3.9
Elbow to grille (I) | 3.6444 |  | Elbow to grille (K) | 3.9
Grill in I | 15 |  | K | 7.15
Total Loss | 130.7905 |  | Grill in K | 15
|  |  | Damper in Duct J | 11.2668
|  |  | Total Loss | 130.9575